section 16400

SWITCHBOARDS – low VOLTAGE

general

Scope

The Contractor shall furnish and install, where indicated, an AMP free-standing, dead-front type low voltage distribution switchboard, utilizing group mounted circuit protective devices, and as shown on the contract drawings.

References

The low voltage distribution switchboards and all components shall be designed, manufactured and tested in accordance with the latest applicable following standards:

UL Standard 891

Submittals – for Review/approval

The following information shall be submitted to the Engineer:

Front view elevation

Floor plan

Top view

Single line

Schematic diagram

Component list

Conduit entry/exit locations

Assembly ratings including:

Short-circuit rating

Voltage

Continuous current

Major component ratings including:

Voltage

Continuous current

Interrupting ratings

Cable terminal sizes

Product data sheets

Where applicable, the following additional information shall be submitted to the Engineer:

Bus connection

Connection details between close-coupled assemblies

Composite floor plan of close-coupled assemblies

Submittals – for construction

The following information shall be submitted for record purposes:

Final as-built drawings and information for items listed in Paragraph 1.04, and shall incorporate all changes made during the manufacturing process

Wiring diagrams

Installation information

Qualifications

The manufacturer of this equipment shall be a local manufacturer that has produced similar electrical equipment for a minimum period of five (10) years. When requested by the engineer, an acceptable list of installations with similar equipment shall be provided demonstrating compliance with this requirement.

Regulatory Requirements

The low-voltage switchboard shall be UL 891 labeled.

Delivery, Storage and Handling

Equipment shall be handled and stored in accordance with manufacturer’s instructions. One (1) copy of these instructions shall be included with the equipment at time of shipment.

Operation and Maintenance Manuals

Equipment operation and maintenance manuals shall be provided with each assembly shipped and shall include instruction leaflets, instruction bulletins and renewal parts lists where applicable, for the complete assembly and each major component.

Products

  - manufacturers

AMP – American Midwest Power

The listing of specific manufacturers above does not imply acceptance of their products that do not meet the specified ratings, features and functions. Manufacturers listed above are not relieved from meeting these specifications in their entirety. Products in compliance with the specification and manufactured by others not named will be considered only if pre-approved by the Engineer ten (10) days prior to bid date.

Ratings

The assembly shall be rated to withstand mechanical forces exerted during short-circuit conditions when connected directly to a power source having available fault current 85,000 amperes symmetrical at rated voltage.

480y/277 Voltage rating as indicated on the drawings.

Switchboard to be rated ____A.

Construction

Switchboards shall consist of the required number of vertical sections bolted together to form a rigid assembly. Each sections structure to be constructed of die formed vertical posts and base members made from galvanized 12 gauge steel that form rigid self supporting structures to support the bussing and over current devices. The sides and rear shall be covered with removable bolt-on 14 gauge covers. All edges of all covers or hinged front panels shall be pan formed. Provide adequate ventilation within the enclosure.

All sections of the switchboard shall be rear aligned with depth as shown on the drawings. All protective devices shall be group mounted. Devices shall be front removable and load connections front accessible enabling switchboard to be mounted against a wall.

The assembly shall be provided with adequate lifting means.

The switchboard shall be equal to AMP “Type F” switchboard utilizing the components herein specified and as shown on the drawings.

Bus

All bus bars shall be tin-plated aluminum or silver plated copper. Main horizontal bus bars shall be mounted with all three phases arranged in the same vertical or horizontal plane. Bus sizing shall be based on NEMA standard temperature rise criteria of 65 degrees C over a 40 degrees C ambient (outside the enclosure).

Provide a full capacity neutral bus where a neutral bus is indicated on the drawings.

All busses to be supported by high strength glass reinforced polyester insulating supports.

A ground bus (minimum 1/4 x 2 inch) shall be furnished firmly secured to each vertical section structure and shall extend the entire length of the switchboard.

All hardware used on conductors shall be high-tensile strength and zinc-plated. All cross bus joints shall be provided with pressed in captive threaded hardware.

Wiring/Terminations

Small wiring, necessary fuse blocks and terminal blocks within the switchboard shall be furnished as required. Control components mounted within the assembly, such as fuse blocks, relays, pushbuttons, switches, etc., shall be suitably marked for identification corresponding to appropriate designations on manufacturer’s wiring diagrams.

Mechanical-type terminals shall be provided for all line and load terminations suitable for copper or aluminum cable rated for 75 degrees C of the size as indicated on the drawings.

Lugs shall be provided in the incoming line section for connection of the main grounding conductor. Additional lugs for connection of other grounding conductors shall be provided as indicated on the drawings.

All control wire shall be bundled and secured with nylon ties. Insulated locking spade terminals shall be provided for all control connections, except where saddle type terminals are provided integral to a device. All current transformer secondary leads shall first be connected to conveniently accessible short-circuit terminal blocks before connecting to any other device. All groups of control wires leaving the switchboard shall be provided with terminal blocks with suitable numbering strips.

Main Protective Devices

Main devises to be either fused main or circuit breaker.

Main devices to be quick make quick break bolted pressure switch for 1200A and above.

Feeder Protective devices

All branch feeder protective devices to be fused distribution switches or molded case circuit breakers.

Circuit breakers must be series rated with main to maintain specified AIC rating of overall assembly.

Switchboards rated 208/120V shall be capable of twin mounting 400A fused switches.

INTEGRATED AUTOmATIC TRANSFER SWITCHES

Where indicated on drawings automatic transfer switches are to be integrated into the switchboard by switchboard manufacturer to form a single integrated assembly with multiple ATS’s group mounted off one continuous emergency bus.

Transfer switches to be cable or hard bus connected to switchboard cross bus

Transfer switches to be cable or hard bus connected to corresponding circuit breaker on the emergency.

Where indicated on drawings as provision for future ATS, an additional section with fully rated cross bus and provisions for future ATS to be included.

Automatic transfer switches to be GE/Zenith type ZTG/ZTS – See Automatic transfer switch specification section.

utility metering

Where indicated on the drawings, furnish a barrier to separate the utility metering compartment complete with hinged sealable door. Bus work shall include provisions for mounting utility company current transformers and potential transformers or potential taps as required by the utility company. Provide service entrance label and provide necessary applicable service entrance features per NEC and local code requirements.

customer metering

Where indicated on the drawings, provide a separate customer metering compartment with a front facing hinged door and include the following:

Current transformers for each meter. Current transformers shall be wired to shorting-type terminal blocks.

Fused potential taps as the potential source for metering as shown on the drawings.

Meter to be digital multifunction type Electro Industries Shark 100 or equal.

Enclosures

NEMA 1 Enclosure - Indoor

Nameplates

Furnish master nameplate giving switchboard designation, voltage ampere rating, short-circuit rating, manufacturer’s name, shop order number, and item number.

Control components mounted within the assembly, such as fuse blocks, relays, pushbuttons, switches, etc., shall be suitably marked for identification corresponding to appropriate designations on manufacturer’s wiring diagrams.

Finish

All exterior and non galvanized interior steel surfaces of the switchboard shall be properly cleaned and provided with an oven baked polyester powder coating paint applied electro-statically. Color and finish of the switchboard shall be ANSI 61 light gray.

- execution

  - Installation

    - The Contractors shall install all equipment per the manufacturer’s instructions, contract drawings and National Electrical Code.

    - The assembly shall be provided with adequate lifting means and shall be capable of being moved into installation position and bolted directly to the floor without the use of floor sills provided the floor is level to 1/8 inch per 3-foot distance in any direction. All necessary hardware to secure the assembly in place shall be provided by the Contractor.

  - field adjustments

    - The Contractor shall perform field adjustments of the protective devices as required to place the equipment in final operating condition. The settings shall be in accordance with the approved short-circuit study, protective device evaluation study and protective device coordination study.

    - Necessary field settings of devices, adjustments and minor modifications to equipment to accomplish conformance with an approved short circuit and protective device coordination study shall be carried out by the Contractor at no additional cost to the owner.